## modbus format
Data format: 9600 8-bit data, 1 stop bit, no checksum
Support modbus protocol 3 6 16. The data format is high bit first, low bit last.
Message protocol format: read register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x03 | Register starting address |  | Number of registers N |  | CRC-16 check
Description: 81-03-00-00-00-7F-1B-EA 81 is the slave address, 03 is the read command, 0000 is the register starting address, 007F means that the number of read registers is 1, that is, the read command. 1BEA is the CRC check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Field definition | ADDR | CMD | Length | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x03 | Data length L=2*N | The value of the first register |  | ...the value of the Nth register |  | CRC-16 check
Note: N is the register data 51 03 FE xx xx... 51 is the slave address, 03 is the read command, FE is the length of the read data,
Message protocol format: write register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x06 | Register address |  | data |  | CRC-16 check
Description: 81-06-01-16-03-E8-76-8C D2 is the slave address, 06 is the instruction to write a single holding register, 000C is the register address, 0001 indicates the host command to discharge the battery, and 9BAA is the CRC check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x06 | Register address |  | data |  | CRC-16 check
Description: 51-06-01-16-03-E8-65-1C Write a single holding register The regular response frame has the same format as the request frame.
Message protocol format: write multiple data registers, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x10 | Register starting address |  | Register length(N) |  | Data content(2N) |  | CRC-16 check
Description: 81-10-01-0B-00-02-00-01-86-A0-DA-FE 0x81 is the slave address, 0x10 means writing multiple data register instructions, 0x01B0 is the register starting address, 0x0002 means continuous Write two registers, 0x0001 represents the data written in the first register, 0x86A0 represents the data written in the second register, and 0xDAFE represents the CRC16 check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x10 | Register starting address |  | Register length(N) |  | CRC-16 check
Description: 51-10-01-0B-00-02-3D-A6 0x51 is the slave address, 0x10 is the instruction to write multiple data registers, 0x010B is the register starting address, 0x0002 means writing two registers continuously, 0x3DA6 means CRC16 Check code.

## Real-time data
BMS UART/RS485 protocol description
Data format: 9600 8-bit data, 1 stop bit, no checksum
Support modbus protocol 3 6 16 | The data format is high bit first, low bit last
address | type of data | Read and write | content | scope | Data calculation instructions
0x00~0x2F | unsigned short int | R | Single battery voltage, every two bytes is a battery voltage | 0--5000 | 0.001 3550*0.001=3.550v
0x30~0x37 |  | R | battery temperature | 0--140 (-40 to 100℃) | The temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x38 |  | R | total battery voltage |  | 0.1V 350*0.1=35.0v
0x39 |  | R | Current data | 0--65535 | 0.1A, 30000 Offset, the charging current is a negative number, and the discharge is a positive number, (30080-30000)*0.1=8A, which is the discharge current
0x3A |  | R | SOC | 0--65535 | 0.001,800/1000=80%
0x3B |  | R | LIFE | 0--65535 | Heartbeat bag
0x3C |  | R | Battery quantity
0x3D |  | R | Battery temperature sensor quantity
0x3E |  | R | Maximum cell voltage | 0--65535 | 1mv
0x3F |  | R | Highest cell voltage serial number | 0--65535 | 1
0x40 |  | R | Minimum cell voltage | 0--65535 | 1mv
0x41 |  | R | Minimum cell voltage serial number | 0--65535 | 1
0x42 |  | R | Maximum and minimum cell voltage difference | 0--65535 | 1mv
0x43 |  | R | Maximum cell temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x44 |  | R | Maximum unit temperature serial number | 0--65535 | 1
0x45 |  | R | Minimum cell temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x46 |  | R | Minimum cell temperature serial number | 0--65535 | 1
0x47 |  | R | Maximum and minimum unit temperature temperature difference | 0--65535 | 1°C
0x48 |  | R | Charge and discharge status | 0--65535 | 0 stationary, 1 charging, 2 discharging
0x49 |  | R | Charger status | 0--65535 | 0: Unable to detect charger 1: Charger detected
0x4A |  | R | Load status | 0--65535 | 0: Unable to detect load 1: Load detected
0x4B |  | R | Battery remaining capacity |  | 0.1AH
0x4C |  | R | Battery cycle times
0x4D |  | R | equilibrium state | 0--65535 | 0: Off 1: Passive balancing 2: Active balancing
0x4F~0x51 |  | R | equilibrium position | 0--65536 | Each bit represents a battery
0x52 |  | R | Charging MOS status | 0--65535 | 0: off 1: on
0x53 |  | R | Discharge MOS status | 0--65535 | 0: off 1: on
0x54 |  | R | Precharge MOS status | 0--65535 | 0: off 1: on
0x55 |  | R | Heating MOS status | 0--65535 | 0: off 1: on
0x56 |  | R | Fan MOS status | 0--65535 | 0: off 1: on
0x57 |  | R | average voltage | 0--65535 | 1mV
0x58 |  | R | power | 0--65535 | W
0x59 |  | R | energy | 0--65535 | 1WH
0x5A |  | R | MOS temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5B |  | R | ambient temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5C |  | R | Heating temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5D |  | R | Heating current | 0--65535 | 1A/bit
0x5F |  | R | Current limiting state | 0--65536 | 1 turns on current limiting 0 turns off current limiting
0x60 |  | R | current limit | 0--65536 | 0.1A/bit offset -30000, less than 30000 is negative, greater than 30000 is positive
0x61~0x63 |  | R | RTC | 0--65536 | Year, month, day/hour, minute and second, for example, 08:30:56 on August 15, 2020, then send 0x14080F081E38
0x64 |  | R | Remaining charging time | 0--65536 | min
0x65 |  | R | DI/DO status | 0--65535 | low byte bit0: DI1 (0:OFF 1:ON) bit1: DI2 (0:OFF 1:ON) bit2: DI3 (0:OFF 1:ON) bit3: DI4 (0:OFF 1:ON) bit4: DI5 (0:OFF 1:ON) bit5: DI6 (0:OFF 1:ON) bit6: DI7 (0:OFF 1:ON) bit7: DI8 (0:OFF 1:ON) high byte bit8:DO1 (0:OFF 1:ON) bit9:DO2 (0:OFF 1:ON) bit10:DO3 (0:OFF 1:ON) bit11:DO4 (0:OFF 1:ON) bit12:DO5 (0:OFF 1:ON) bit13:DO6 (0:OFF 1:ON) bit14:DO7 (0:OFF 1:ON) bit15:DO8 (0:OFF 1:ON)
0x6B |  | R | Wake-up source | 0--65536 | bit0: key bit1: button bit2：485 bit3：can bit4: current"
0x6C |  | R | xxx | 0--65536 | reserved
0x6D |  | R | New fault code 0-1 | 0--65536 | Low byte: bit2:0, single overvoltage alarm level bit5:3, single unit undervoltage alarm level bit6, smart charger connection bit7, smart charger connection failed high byte bit2:0, excessive pressure difference alarm level bit5:3, charging high temperature alarm level bit6, intelligent discharge device connection bit7, smart discharge device connection failed | The new fault code is exclusive to K version Alarms with alarm levels consist of three bits. B000 means no alarm. B001~B111 are level 1~level 7 alarms. The police without police level is composed of one bit. B0, no alarm B1, there is an alarm
0x6E |  | R | New fault code 2-3 | 0--65536 | low byte bit2:0, charging low temperature alarm level bit5:3, discharge high temperature alarm level bit6, charging mos temperature is too high bit7, charging mos temperature detection failure high byte bit2:0, discharge low temperature alarm level bit5:3, excessive temperature difference alarm level bit6, discharge mos temperature is too high bit7, discharge mos temperature detection fault
0x6F |  | R | New fault code 4-5 | 0--65536 | low byte bit2:0, total voltage is too high alarm level bit5:3, total voltage is too low alarm level bit6, short circuit protection bit7, reserved high byte bit2:0, charging overcurrent alarm level bit5:3, discharge overcurrent alarm level bit6, low voltage prohibits charging bit7 high voltage discharging prohibited
0x70 |  | R | New fault code 6-7 | 0--65536 | low byte bit2:0, soc is too low alarm level bit5:3, soh is too low alarm level bit6, parallel communication successful bit7, parallel communication failed high byte bit2:0, MOS temperature too high alarm level bit5:3, thermal runaway alarm level bit6, reserved bit7,reserved
0x71 |  | R | New fault code 8-9 | 0--65536 | low byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved high byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved
0x72 |  | R | New fault code 10-11 | 0--65536 | low byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved high byte bit0, afe chip failure bit1, afe communication failure bit2, afe sampling failure bit3, voltage detection failure bit4, the voltage collection line is disconnected bit5, total voltage detection failure bit6, current detection fault bit7, temperature detection failure
0x73 |  | R | New fault code 12-13 | 0--65536 | low byte bit,0, the temperature acquisition line is disconnected bit1, eeprom failure bit2, flash failure bit3, rtc failure bit4, charging mos failure bit5, discharge mos fault bit6, precharge mos failure bit7, precharge failed high byte bit0, communication command controls charging mos off bit1, communication command controls discharge mos off bit2, switch control charging mos off bit3, switch control discharge mos off bit4, fan working bit5, heating work bit6, current limiting module works bit7, heating failure
0x7c |  | R | Reserved signal 19 | 0--65536
0x7d |  | R | Reserved signal 20 | 0--65536
0x7e |  | R | Communication interface type | 0--65537 | 1:485 2: UART